## Sheet1
How much heat is lost in the transport piping?
In steady state ICSF operation, we observed ICSF adding ~300W to the coolant
start with geometry | pipe length | 1.8 | m |  |  | from ICSF to between-circuits heat exchanger, roughly
| pipe ID | 0.375 | in |  |  | PEX
|  | 0.009525 | m
| x-sect | 7.1256e-05 | m2
|  | 71.2557 | mm2
|  | 0.71256 | cm2
and state conditions |  | 2 | ml/s
mass flow | m_dot | 2 | g/s
| velocity | 0.028068 | m/s
|  | 0.091782 | fps
| residence time | 64.1302 | s
| total mass | 128.2603 | g
initial temperature conditions | T_ambient | 25 | °C
| T_ICSF_out | 90 | °C |  |  | http://en.wikipedia.org/wiki/Lumped_capacitance_model
consider insulation properties | k_insul | 0.037 | W/m-K |  |  | http://www.engineeringtoolbox.com/thermal-conductivity-d_429.html
| thk_insul | 1.5 | in
insulation radii | r_o | 44.4501 | mm | 1.75 | in
| r_i | 6.35 | mm | 0.25 | in
and coolant properties | c_p | 4.187 | J/g-K
| R_insul_tot | 4.6502 | K/W |  |  | http://archbps1.campus.tue.nl/bpswiki/images/5/53/H8.pdf
thermal conductivity of the pipe | UA | 0.21505 | W/K |  |  | these numbers jive with the example on page 94 of InD, more or less
(assume lumped capacitance model)
thermal time constant | tau | 2497.2614 | s | 41.621
amount of time to lose 60% | 5tau | 12486.3069 | s
effectiveness-NTU method
| Cmin | 8.374 | W/K |  |  | m_dot*c_p
| q_max | 544.31 | W
| NTU | 0.02568
| effectiveness | 2.535%
| q_loss_effNTU | 13.8 | W |  |  | eqn 11.23 (Inc & D 4th)
| T_outlet_effNTU | 89.9984 | °C
heat loss per meter max | q_lossperm_engTB | 6 | W/m |  |  | http://www.engineeringtoolbox.com/heat-loss-insulated-pipes-d_1151.html
| q_lossperm_engTB | 10.8 | W
| T_outlet | 89.9799 | °C
constant wall method | T_outlet_CW | 88.352 | °C
[5 empty] | delLength | 0.1 | m |  | rate of heat loss (W)
[5 empty] | delTime | 3.5628 | s |  | 65.6681
[5 empty] | length | time (s) | heat loss (J) | Temperature (°C) | Heat Loss (cumulative)
|  | 64.1302 | 300 |  | 0 | 0 | 0 | 90 | 0
|  | 64.1302 | 0 |  | 0.1 | 3.5628 | 4.9801 | 89.8331 | 4.9801
[5 empty] | 0.2 | 7.1256 | 4.9673 | 89.6666 | 9.9473
[5 empty] | 0.3 | 10.6884 | 4.9545 | 89.5005 | 14.9018
[5 empty] | 0.4 | 14.2511 | 4.9418 | 89.3349 | 19.8436
[5 empty] | 0.5 | 17.8139 | 4.9291 | 89.1697 | 24.7727
[5 empty] | 0.6 | 21.3767 | 4.9164 | 89.0049 | 29.6892
[5 empty] | 0.7 | 24.9395 | 4.9038 | 88.8405 | 34.593
[5 empty] | 0.8 | 28.5023 | 4.8912 | 88.6766 | 39.4842
[5 empty] | 0.9 | 32.0651 | 4.8787 | 88.513 | 44.3629
[5 empty] | 1 | 35.6279 | 4.8661 | 88.3499 | 49.229
[5 empty] | 1.1 | 39.1907 | 4.8536 | 88.1873 | 54.0827
[5 empty] | 1.2 | 42.7534 | 4.8412 | 88.025 | 58.9238
[5 empty] | 1.3 | 46.3162 | 4.8287 | 87.8631 | 63.7526
[5 empty] | 1.4 | 49.879 | 4.8163 | 87.7017 | 68.5689
[5 empty] | 1.5 | 53.4418 | 4.804 | 87.5407 | 73.3729
[5 empty] | 1.6 | 57.0046 | 4.7916 | 87.3801 | 78.1645
[5 empty] | 1.7 | 60.5674 | 4.7793 | 87.2199 | 82.9439
[5 empty] | 1.8 | 64.1302 | 4.7671 | 87.0601 | 87.7109
[5 empty] | 1.9 | 67.693 | 4.7548 | 86.9007 | 92.4657
[5 empty] | 2 | 71.2557 | 4.7426 | 86.7418 | 97.2083
[5 empty] | 2.1 | 74.8185 | 4.7304 | 86.5832 | 101.9388
[5 empty] | 2.2 | 78.3813 | 4.7183 | 86.4251 | 106.657
[5 empty] | 2.3 | 81.9441 | 4.7062 | 86.2673 | 111.3632
[5 empty] | 2.4 | 85.5069 | 4.6941 | 86.11 | 116.0573
[5 empty] | 2.5 | 89.0697 | 4.682 | 85.9531 | 120.7393
[5 empty] | 2.6 | 92.6325 | 4.67 | 85.7965 | 125.4093
[5 empty] | 2.7 | 96.1952 | 4.658 | 85.6404 | 130.0673
[5 empty] | 2.8 | 99.758 | 4.646 | 85.4847 | 134.7133
[5 empty] | 2.9 | 103.3208 | 4.6341 | 85.3294 | 139.3475
[5 empty] | 3 | 106.8836 | 4.6222 | 85.1744 | 143.9697
[5 empty] | 3.1 | 110.4464 | 4.6103 | 85.0199 | 148.58
[5 empty] | 3.2 | 114.0092 | 4.5985 | 84.8658 | 153.1785
[5 empty] | 3.3 | 117.572 | 4.5867 | 84.712 | 157.7652
[5 empty] | 3.4 | 121.1348 | 4.5749 | 84.5587 | 162.3401
[5 empty] | 3.5 | 124.6975 | 4.5632 | 84.4057 | 166.9033
[5 empty] | 3.6 | 128.2603 | 4.5514 | 84.2532 | 171.4547
[5 empty] | 3.7 | 131.8231 | 4.5398 | 84.101 | 175.9945
[5 empty] | 3.8 | 135.3859 | 4.5281 | 83.9493 | 180.5226
[5 empty] | 3.9 | 138.9487 | 4.5165 | 83.7979 | 185.0391
[5 empty] | 4 | 142.5115 | 4.5049 | 83.6469 | 189.544
[5 empty] | 4.1 | 146.0743 | 4.4933 | 83.4963 | 194.0373
[5 empty] | 4.2 | 149.6371 | 4.4818 | 83.3461 | 198.519
[5 empty] | 4.3 | 153.1998 | 4.4703 | 83.1962 | 202.9893
[5 empty] | 4.4 | 156.7626 | 4.4588 | 83.0468 | 207.4481
[5 empty] | 4.5 | 160.3254 | 4.4473 | 82.8977 | 211.8954
[5 empty] | 4.6 | 163.8882 | 4.4359 | 82.749 | 216.3313
[5 empty] | 4.7 | 167.451 | 4.4245 | 82.6007 | 220.7558
[5 empty] | 4.8 | 171.0138 | 4.4132 | 82.4528 | 225.169
[5 empty] | 4.9 | 174.5766 | 4.4018 | 82.3053 | 229.5708
[5 empty] | 5 | 178.1393 | 4.3905 | 82.1581 | 233.9613
[5 empty] | 5.1 | 181.7021 | 4.3792 | 82.0113 | 238.3406
[5 empty] | 5.2 | 185.2649 | 4.368 | 81.8649 | 242.7086
[5 empty] | 5.3 | 188.8277 | 4.3568 | 81.7189 | 247.0653
[5 empty] | 5.4 | 192.3905 | 4.3456 | 81.5732 | 251.4109
[5 empty] | 5.5 | 195.9533 | 4.3344 | 81.4279 | 255.7454
[5 empty] | 5.6 | 199.5161 | 4.3233 | 81.283 | 260.0687
[5 empty] | 5.7 | 203.0789 | 4.3122 | 81.1385 | 264.3809
[5 empty] | 5.8 | 206.6416 | 4.3011 | 80.9943 | 268.682
[5 empty] | 5.9 | 210.2044 | 4.2901 | 80.8505 | 272.9721
[5 empty] | 6 | 213.7672 | 4.2791 | 80.7071 | 277.2511
[5 empty] | 6.1 | 217.33 | 4.2681 | 80.5641 | 281.5192
[5 empty] | 6.2 | 220.8928 | 4.2571 | 80.4214 | 285.7763
[5 empty] | 6.3 | 224.4556 | 4.2462 | 80.279 | 290.0225
[5 empty] | 6.4 | 228.0184 | 4.2353 | 80.1371 | 294.2578
[5 empty] | 6.5 | 231.5812 | 4.2244 | 79.9955 | 298.4822
[5 empty] | 6.6 | 235.1439 | 4.2136 | 79.8543 | 302.6957
[5 empty] | 6.7 | 238.7067 | 4.2027 | 79.7134 | 306.8984
[5 empty] | 6.8 | 242.2695 | 4.1919 | 79.5729 | 311.0904
[5 empty] | 6.9 | 245.8323 | 4.1812 | 79.4328 | 315.2716
[5 empty] | 7 | 249.3951 | 4.1704 | 79.293 | 319.442
[5 empty] | 7.1 | 252.9579 | 4.1597 | 79.1535 | 323.6017
[5 empty] | 7.2 | 256.5207 | 4.149 | 79.0145 | 327.7508
[5 empty] | 7.3 | 260.0834 | 4.1384 | 78.8758 | 331.8891
[5 empty] | 7.4 | 263.6462 | 4.1278 | 78.7374 | 336.0169
[5 empty] | 7.5 | 267.209 | 4.1172 | 78.5994 | 340.1341
[5 empty] | 7.6 | 270.7718 | 4.1066 | 78.4618 | 344.2407
[5 empty] | 7.7 | 274.3346 | 4.096 | 78.3245 | 348.3367
[5 empty] | 7.8 | 277.8974 | 4.0855 | 78.1875 | 352.4222
[5 empty] | 7.9 | 281.4602 | 4.075 | 78.0509 | 356.4973
[5 empty] | 8 | 285.023 | 4.0646 | 77.9147 | 360.5618
[5 empty] | 8.1 | 288.5857 | 4.0541 | 77.7788 | 364.616
[5 empty] | 8.2 | 292.1485 | 4.0437 | 77.6433 | 368.6597
[5 empty] | 8.3 | 295.7113 | 4.0333 | 77.5081 | 372.693
[5 empty] | 8.4 | 299.2741 | 4.023 | 77.3733 | 376.716
[5 empty] | 8.5 | 302.8369 | 4.0126 | 77.2388 | 380.7286
[5 empty] | 8.6 | 306.3997 | 4.0023 | 77.1046 | 384.731
[5 empty] | 8.7 | 309.9625 | 3.9921 | 76.9708 | 388.723
[5 empty] | 8.8 | 313.5253 | 3.9818 | 76.8373 | 392.7048
[5 empty] | 8.9 | 317.088 | 3.9716 | 76.7042 | 396.6764
[5 empty] | 9 | 320.6508 | 3.9614 | 76.5714 | 400.6378
[5 empty] | 9.1 | 324.2136 | 3.9512 | 76.439 | 404.589
[5 empty] | 9.2 | 327.7764 | 3.9411 | 76.3069 | 408.5301
[5 empty] | 9.3 | 331.3392 | 3.9309 | 76.1752 | 412.461
[5 empty] | 9.4 | 334.902 | 3.9209 | 76.0437 | 416.3819
[5 empty] | 9.5 | 338.4648 | 3.9108 | 75.9127 | 420.2927
[5 empty] | 9.6 | 342.0275 | 3.9007 | 75.7819 | 424.1934
[5 empty] | 9.7 | 345.5903 | 3.8907 | 75.6515 | 428.0841
[5 empty] | 9.8 | 349.1531 | 3.8807 | 75.5214 | 431.9649
[5 empty] | 9.9 | 352.7159 | 3.8708 | 75.3917 | 435.8356
[5 empty] | 10 | 356.2787 | 3.8608 | 75.2623 | 439.6965
[5 empty] | 10.1 | 359.8415 | 3.8509 | 75.1332 | 443.5474
[5 empty] | 10.2 | 363.4043 | 3.841 | 75.0045 | 447.3884
[5 empty] | 10.3 | 366.9671 | 3.8312 | 74.8761 | 451.2195
[5 empty] | 10.4 | 370.5298 | 3.8213 | 74.748 | 455.0409
[5 empty] | 10.5 | 374.0926 | 3.8115 | 74.6202 | 458.8524
[5 empty] | 10.6 | 377.6554 | 3.8017 | 74.4928 | 462.6541
[5 empty] | 10.7 | 381.2182 | 3.792 | 74.3657 | 466.446
[5 empty] | 10.8 | 384.781 | 3.7822 | 74.2389 | 470.2283
[5 empty] | 10.9 | 388.3438 | 3.7725 | 74.1125 | 474.0008
[5 empty] | 11 | 391.9066 | 3.7628 | 73.9864 | 477.7636
[5 empty] | 11.1 | 395.4694 | 3.7532 | 73.8606 | 481.5167
[5 empty] | 11.2 | 399.0321 | 3.7435 | 73.7351 | 485.2602
[5 empty] | 11.3 | 402.5949 | 3.7339 | 73.6099 | 488.9941
[5 empty] | 11.4 | 406.1577 | 3.7243 | 73.4851 | 492.7185
[5 empty] | 11.5 | 409.7205 | 3.7147 | 73.3606 | 496.4332
[5 empty] | 11.6 | 413.2833 | 3.7052 | 73.2364 | 500.1384
[5 empty] | 11.7 | 416.8461 | 3.6957 | 73.1125 | 503.8341
[5 empty] | 11.8 | 420.4089 | 3.6862 | 72.989 | 507.5203
[5 empty] | 11.9 | 423.9716 | 3.6767 | 72.8657 | 511.1971
[5 empty] | 12 | 427.5344 | 3.6673 | 72.7428 | 514.8643
[5 empty] | 12.1 | 431.0972 | 3.6579 | 72.6202 | 518.5222
[5 empty] | 12.2 | 434.66 | 3.6485 | 72.4979 | 522.1707
[5 empty] | 12.3 | 438.2228 | 3.6391 | 72.3759 | 525.8098
[5 empty] | 12.4 | 441.7856 | 3.6298 | 72.2543 | 529.4396
[5 empty] | 12.5 | 445.3484 | 3.6204 | 72.1329 | 533.06
[5 empty] | 12.6 | 448.9112 | 3.6112 | 72.0119 | 536.6712
[5 empty] | 12.7 | 452.4739 | 3.6019 | 71.8912 | 540.2731
[5 empty] | 12.8 | 456.0367 | 3.5926 | 71.7707 | 543.8657
[5 empty] | 12.9 | 459.5995 | 3.5834 | 71.6506 | 547.4491
[5 empty] | 13 | 463.1623 | 3.5742 | 71.5308 | 551.0233
[5 empty] | 13.1 | 466.7251 | 3.565 | 71.4113 | 554.5883
[5 empty] | 13.2 | 470.2879 | 3.5559 | 71.2922 | 558.1442
[5 empty] | 13.3 | 473.8507 | 3.5467 | 71.1733 | 561.6909

## Sheet2
75
1.8862
| 5 | m
| 3 | [30 empty] | 34 | 35 | 36 | 37
position
inlet
1
time | 0 | 0.14706 | 0.29412 | 0.44118 | 0.58824 | 0.73529 | 0.88235 | 1.0294 | 1.1765 | 1.3235 | 1.4706 | 1.6176 | 1.7647 | 1.9118 | 2.0588 | 2.2059 | 2.3529 | 2.5 | 2.6471 | 2.7941 | 2.9412 | 3.0882 | 3.2353 | 3.3824 | 3.5294 | 3.6765 | 3.8235 | 3.9706 | 4.1176 | 4.2647 | 4.4118 | 4.5588 | 4.7059 | 4.8529 | 5
0 | 90 | 89.9116 | 89.8234 | 89.7352 | 89.6472 | 89.5593 | 89.4716 | 89.3839 | 89.2964 | 89.209 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618
1 | 89.9116 | 89.8234 | 89.7352 | 89.6472 | 89.5593 | 89.4716 | 89.3839 | 89.2964 | 89.209 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775
2 | 89.8234 | 89.7352 | 89.6472 | 89.5593 | 89.4716 | 89.3839 | 89.2964 | 89.209 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932
3 | 89.7352 | 89.6472 | 89.5593 | 89.4716 | 89.3839 | 89.2964 | 89.209 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091
4 | 89.6472 | 89.5593 | 89.4716 | 89.3839 | 89.2964 | 89.209 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725
5 | 89.5593 | 89.4716 | 89.3839 | 89.2964 | 89.209 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411
6 | 89.4716 | 89.3839 | 89.2964 | 89.209 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573
7 | 89.3839 | 89.2964 | 89.209 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736
8 | 89.2964 | 89.209 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39
9 | 89.209 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39 | 86.3066
10 | 89.1217 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39 | 86.3066 | 86.2232
11 | 89.0345 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39 | 86.3066 | 86.2232 | 86.14
12 | 88.9475 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39 | 86.3066 | 86.2232 | 86.14 | 86.0569
13 | 88.8605 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39 | 86.3066 | 86.2232 | 86.14 | 86.0569 | 85.9739
14 | 88.7737 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39 | 86.3066 | 86.2232 | 86.14 | 86.0569 | 85.9739 | 85.891
15 | 88.687 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39 | 86.3066 | 86.2232 | 86.14 | 86.0569 | 85.9739 | 85.891 | 85.8082
16 | 88.6004 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39 | 86.3066 | 86.2232 | 86.14 | 86.0569 | 85.9739 | 85.891 | 85.8082 | 85.7255
17 | 88.5139 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39 | 86.3066 | 86.2232 | 86.14 | 86.0569 | 85.9739 | 85.891 | 85.8082 | 85.7255 | 85.643
18 | 88.4276 | 88.3414 | 88.2552 | 88.1692 | 88.0834 | 87.9976 | 87.9119 | 87.8264 | 87.741 | 87.6557 | 87.5705 | 87.4855 | 87.4005 | 87.3157 | 87.2309 | 87.1463 | 87.0618 | 86.9775 | 86.8932 | 86.8091 | 86.725 | 86.6411 | 86.5573 | 86.4736 | 86.39 | 86.3066 | 86.2232 | 86.14 | 86.0569 | 85.9739 | 85.891 | 85.8082 | 85.7255 | 85.643 | 85.5605
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99

## Sheet3
39.37 | m2in
1000000 | rho | g/m3
| 128.2603 | g
| 5.0431 | a box this cm on each side
| 0.050431 | this m on each side
| 0.01526 | m2 of that box
| 0.037 | W/m-k